HVAC Guide Specifications (Water Loop)

Packaged Water Source Heat Pumps

Size Range:

1.8 to 21.1 kW

Carrier Unit:

50PCH,PCV Series 50 Hz

Part 1 — General

1.01 SYSTEM DESCRIPTION

A. 	Install water source heat pumps, as indicated on the plans with capacities and characteristics as listed in the schedule and the specifications that follow. Units shall be horizontal or vertical configurations. All equipment shall be rated and certified in accordance with AHRI/ISO (Air-Conditioning, Heating, and Refrigeration Institute/International Organization for Standardization) 13256-1. All equipment shall be tested, investigated, and determined to comply with the requirements of the standards for Heating and Cooling Equipment UL-1995 for the United States and CAN/CSA-C22.2 NO.236 for Canada, by Intertek Testing Laboratories (ETL). The units shall have AHRI/ISO, ETL-US-C labels and CE community mark.

B. 	Units shall be supplied completely factory built and capable of operation with an entering water temperature range from 6.7 to 43.3 C. Quality control system shall automatically perform via computer: triple leak check, pressure tests, evacuation and accurately charging of system, detailed heating and cooling mode tests, and quality cross checking all operational and test conditions to pass/fail criteria.

C. 	Units shall be individually packaged on wooden skid with protective corner posts and plastic stretch wrapping for maximum protection.

1.02 QUALITY ASSURANCE

A. 	All equipment listed in this section must be rated in accordance with AHRI/ASHRAE/ISO 13256-1 performance standard, latest edition. The applicable units shall have a AHRI/ISO label. Standard cabinet panel insulation shall meet NFPA (National Fire Protection Association, U.S.A Standard) 90A requirements, air erosion and mold growth limits of UL-181, stringent fungal resistance test per ASTMC1071 (American Society for Testing and Materials) and ASTM G21, and shall meet zero level bacteria growth per ASTM G22.

B. 	All units shall be factory tested in all operating modes and safety switch operation shall be verified.

C. 	Serial numbers will be recorded by factory and furnished to contractor for ease of unit warranty status.

Part 2 — Product

2.01 EQUIPMENT

A. 	General: Units shall be prewired and precharged in factory.

B. 	Basic Construction:

1. 	Units shall have the air flow arrangement as shown on the plans. If units with these arrangements are not used, the contractor supplying the water source heat pumps is responsible for any extra costs incurred by other trades and must submit detailed mechanical drawings showing ductwork requirements and changes or relocation of any other mechanical or electrical system. If other arrangements make servicing difficult, the contractor must provide access panels and clear routes to ease service. The architect must approve all changes 10 days prior to bid.

2. 	All units shall have stainless steel drain pans to comply with this project’s IAQ (indoor air quality) requirements. Painted steel or plastic is not acceptable.

3. 	The cabinet shall be fabricated from heavy gage galvanized steel for superior corrosion protection. All interior surfaces shall be lined with 1/2-in.. thick, multi-density, coated, fiberglass insulation. Insulation must be non-combustible, non-hydroscopic and anti-fungal. Insulation must meet NFPA 90A and 90B for fire protection as well as Fire Hazard classification 25/50 (per ASTM E84 and UL 723 and CAN/ULC S102-M88), ASTM C1071, erosion requirements of UL181 and be certified to meet GREENGUARD indoor air quality standards for low emitting products. One blower access panel and two compressor compartment access panels shall be removable with supply and return air ductwork in place.

4. 	Unit shall have a floating compressor or pan consisting of a 1/2-in. (12 mm) thick high density elastomeric pad between the compressor base plate and the unit base pan to prevent transmission of vibration to the structure.

5. 	Units shall have a 2.54 cm filter rack and 2.54 cm thick throwaway type glass fiber filter as standard. The filter rack shall incorporate a 2.54 cm duct flange. The units shall have an insulated divider panel between the air-handling section and the compressor section to minimize the transmission of compressor noise, and to permit service testing without air bypass.

6. 	Cabinets shall have separate holes and knockouts for entrance of line voltage and low voltage control wiring. Supply and return water connections shall be brass female pipe thread fittings and mounted flush to cabinet exterior. Connections that require a backup wrench or that extrude past the unit corner post are not acceptable. Condensate connection will be stainless steel female pipe thread fittings. Plastic is not acceptable.

7. 	Hanging brackets shall be provided as standard for horizontal units.

C. 	Fan and Motor Assembly:

1. 	The fan shall be direct-drive centrifugal forward curved type with a dynamically balanced wheel. The housing and wheel shall be designed for quiet low velocity operation. The blower housing shall feature a removable inlet ring to facilitate removal and servicing of the fan motor. The fan motor shall be 3-speed, permanently lubricated, PSC (permanent split capacitor) type with thermal overload protection.

2. 	Units rated 4.4 to 21.1 kW shall have an optional electronically commutated motor (ECM) to comply with necessary CE requirements.

3. 	Blower shall have inlet rings to allow removal of wheel and motor from one side without removing housing.

4. 	Units supplied without permanently lubricated motors must provide external oilers for easy service.

5. 	The fan and motor assembly must be capable of overcoming the external static pressures as shown on the schedule.

6. 	The airflow/static pressure rating of the unit shall be based on a wet coil and a clean filter in place.

D. 	Refrigerant Components:

1. 	Units shall use R-410A refrigerant. All units shall have a factory sealed and fully charged refrigerant circuit.

2. 	Hermetic Compressor:

Hermetic reciprocating, rotary, or scroll compressors shall be specifically designed for R-410A refrigerant and shall be internally sprung (if reciprocating), externally isolated and with thermal overload protection.

3. 	Refrigerant metering thermostatic expansion valves or capillary tubes.

4. 	The finned tube heat exchanger shall be constructed of lanced aluminum fins not exceeding 6.3 fins per cm bonded to rifled copper tubes in a staggered pattern and will have a 600 psig (4140 kPa) working pressure. The heat exchanger shall have aluminum end sheets.

5. 	Reversing Valve:

Reversing valves shall be four-way solenoid activated refrigerant valves that shall fail to the heating operation should the solenoid fail to function. Reversing valves that fail to the cooling operation shall not be allowed.

6. 	Coaxial (tube in tube) refrigerant to water heat exchanger. Refrigerant to water heat exchangers shall be of copper inner water tube and steel outer refrigerant tube design rated to withstand 600 psig (4140 kPa) working refrigerant pressure and 400 psig (2758 kPa) working water pressure. Shell and tube style refrigerant to water heat exchangers shall be treated as pressure vessels and shall require refrigerant pressure relief valves piped to the exterior of the building. The contractor supplying the water source heat pumps with shell and tube heat exchangers shall be responsible for any additional installation costs. Brazed plate water to refrigerant heat exchangers shall require additional centrifugal separators added to the supply water piping at each unit. Each separator shall have an automated clean out valve piped to a waste line. The contractor supplying water source heat pumps with brazed plate heat exchangers shall be responsible for any additional costs.

7. 	Safety controls include both a high pressure and low pressure switch. Temperature sensors shall not replace these safety switches. See the unit controls section.

8. 	Access fittings shall be factory installed on high and low pressure refrigerant lines to facilitate field service.

9. 	Activation of any safety device shall prevent compressor operation via a lockout circuit. The lockout circuit shall be reset at the thermostat or at the contractor supplied disconnect switch. Units which may be reset at the disconnect switch only shall not be acceptable.

E. 	Controls and Safeties:

1. 	Electrical:

Controls and safety devices will be factory wired and mounted within the unit. Controls shall include fan relay, compressor contactor, 24-v transformer, reversing valve coil, solid-state lockout controller and unit protection module (UPM). The standard transformer shall be rated for a minimum 50 va. All units shall be nameplated for use with time-delay fuses or HACR (Heating, Air Conditioning and Refrigeration) circuit breakers. Unit controls shall be 24-v and provide heating or cooling as required by the remote thermostat/sensor.

2. 	Piping:

a. 	Supply and return water connections shall be copper FPT fittings and shall be securely mounted flush to the cabinet corner post allowing for connection to a flexible hose without the use of a backup wrench.

b. 	All water connections and electrical knockouts must be in the compressor compartment corner post to not interfere with the serviceability of unit. Contractor shall be responsible for any extra costs involved in the installation of units that do not have this feature.

3. 	Unit Controls:

a. 	Solid-State Safety Circuit:

All units shall have a Complete C board safety control circuit with the following features:

1) 	Anti-short cycle time delay (5-minute delay on break).

2) 	Random start time delay on initial power.

3) 	Brown out/surge/power interruption protection.

4) 	120-second low pressure switch bypass timer.

5) 	High refrigerant pressure shutdown.

6) 	Low refrigerant pressure shutdown.

7) 	Low water temperature shutdown (adjustable for closed loop systems).

8) 	Air coil freeze protection shutdown.

9) 	High condensate level shutdown.

10) 	24 vac alarm output for remote fault indication.

b. 	The Complete C board shall automatically reset after a safety shutdown. Restart the unit if the cause of the shutdown no longer exists (except for low temperature and high condensate level shutdowns). Should a fault re-occur within 60 minutes after reset, then a “hard” lockout will occur. A light-emitting diode (LED) shall annunciate the following alarms: brown out, high refrigerant pressure, low refrigerant pressure, low water temperature and a high level of condensate in the drain pan. The LED will display each fault condition as soon as the fault occurs. If a hard lockout occurs, then the fault LED will display the type of fault until the unit is reset.

c. 	The Complete C board shall feature the following field configurable adjustments:

1) 	Lock out reset on thermostat interruption or power reset.

2) 	Two or four restart attempts before a hard lockout.

3) 	Test mode (reduces all time delays to 5 seconds for diagnostic work).

4) 	Antifreeze setting for low water temperature sensor.

d. 	Safety devices include:

1) 	Low pressure cutout set a 40 psig (280 kPa) for loss of charge protection (freezestat and/or high discharge gas temperature sensor is not acceptable).

2) 	High pressure cutout control set at 600 psig (4125 kPa).

3) 	Low supply water temperature sensor that detects drops in refrigerant temperature that could result in water coax heat exchanger freezing.

4) 	Low air coil temperature sensor that detects drops in refrigerant temperature that could result in air heat exchanger freezing.

5) 	High level condensate sensor that shuts off the compressor if the condensate drain pan fills with water.

6) 	On board voltage detection that disables the compressor control circuit if there are extreme variations in supply voltage.

F. 	Special Features:

1. 	Cupronickel coaxial water-to-refrigerant heat exchangers shall be provided.

2. 	Carrier commercial thermostat controls are available as follows:

Edge® Pro 7-day programmable thermostat offers 2-stage heat, 2-stage cool, remote contact input, remote sensor capability, pre-occupancy purge, soft start, manual/auto changeover, 4 settings per day, 24 vac, backlit LCD, keypad lockout, no batteries required, 5- minute compressor protection, never lost memory, 3 security levels, and temperature display in degrees F or C.

3. 	Aquazone system control panel as specified in the 50RLP Product Data is available.

4. 	Sound attenuation (mute) package shall consist of high technology compressor blanket on sizes 018 and above.