HVAC Guide Specifications

Outdoor Air-Cooled Liquid Chiller

Size Range:

140 to 350 Tons, Nominal

(490 to 1230 kW, Nominal)

Carrier Model Number:

30XA with Greenspeed® Intelligence

Part 1 — General

1.01	SYSTEM DESCRIPTION

Microprocessor controlled, air-cooled liquid chiller for outdoor installation, utilizing variable speed screw compressors and low sound variable speed fans.

1.02	QUALITY ASSURANCE

A.	Unit shall be rated in accordance with AHRI (Air-Conditioning, Heating and Refrigeration Institute) Standard 550/590 (U.S.A.) latest edition and all units shall be ASHRAE (American Society of Heating, Refrigerating, and Air-Conditioning Engineers) 90.1 compliant.

B.	Unit construction shall comply with ASHRAE 15 Safety Code, UL (Underwriters Laboratories) 1995, and ASME (American Society of Mechanical Engineers) applicable codes (U.S.A. codes).

C.	Unit shall be manufactured in a facility registered to ISO (International Organization for Standardization) 9001 Manufacturing Quality Standard.

D.	Unit shall be full load run tested at the factory.

1.03	DELIVERY, STORAGE AND HANDLING

A.	Unit controls shall be capable of withstanding 150 F (65.5 C) storage temperatures in the control compartment.

B.	Unit shall be stored and handled per unit manufacturer’s recommendations.

Part 2 — Products

2.01	EQUIPMENT

A.	General:

Factory assembled, single-piece chassis, air-cooled liquid chiller. Contained within the unit cabinet shall be all factory wiring, piping, controls, refrigerant charge (R-134a), and special features required prior to field start-up.

B.	Materials of Construction:

1.	The base rail is industrial-quality, 7 ga, zinc-dipped galvanized frame (with Magni-coated screws).

2.	Cabinet shall be galvanized steel casing with a baked enamel powder or pre-painted finish.

3.	Cabinet shall be capable of withstanding 500-hour salt spray test in accordance with the ASTM (American Society for Testing and Materials) (U.S.A.) B-117 standard.

C.	Fans:

1.	Condenser fans shall be variable-speed, 9-blade airfoil cross-section, reinforced polymer construction, shrouded-axial type, and shall be statically and dynamically balanced with inherent corrosion resistance.

2.	The variable speed drives for the condenser fans shall include a DC link reactor.

3.	Air shall be discharged vertically upward.

4.	Fans shall be protected by coated steel wire safety guards.

D.	Compressor/Compressor Assembly:

1.	Comprised of semi-hermetic twin screw type compressors.

2.	Compressor motor shall be direct drive, VFD (variable frequency drive) controlled to match the load requirement, with a maximum speed of 3500 rpm. The motors are protected by motor temperature sensors, and are suction gas cooled.

3.	Capacity control shall utilize a VFD to unload the compressors from 100% to 50% of full load. Below 50% load, the combination of VFD and slide valves will unload the compressors to 12% of full load.

4.	The VFD for each compressor motor shall include a DC link reactor.

E.	Flooded Cooler:

1.	Shall be mechanically cleanable tubes in a shell-and-tube type cooler with removable heads.

2.	Tubes shall be internally enhanced seamless-copper type rolled into tube sheets.

3.	Shall be equipped with Victaulic-type water connections.

4.	Shell and cooler heads shall be insulated with  3/4-in. PVC foam (closed-cell) with a maximum K factor of 0.28.

5.	Design shall incorporate a minimum of 2 or 3 independent refrigerant circuits.

6.	Cooler shall be tested and stamped in accordance with ASME Code for a refrigerant working side pressure of 220 psig (1517 kPa). Cooler shall have a maximum water-side pressure of 300 psig (2068 kPa).

7.	Cooler shall have a cooler drain and vent.

8.	Low-ambient temperature protection: unit shall have factory-installed cooler heater (where applicable), and pumpout cycle to protect cooler from ambient temperature freeze down to 0° F (–17.8 C).

9.	Cooler shall be provided with a factory-installed flow switch.

F.	Condenser:

1.	Coil shall be air-cooled Novation® heat exchanger technology (MCHX) and shall have a series of flat tubes containing a series of multiple, parallel flow microchannels layered between the refrigerant manifolds. Novation coils shall consist of a two-pass arrangement. Coil construction shall consist of aluminum alloys for fins, tubes, and manifolds in combination with a corrosion-resistant coating.

2.	Tubes shall be cleaned, dehydrated, and sealed.

3.	Assembled condenser coils shall be pressure tested at the coil factory at 660 psig (5448 kPa) and subsequently shall be leak tested at 145 psig ±5 psig (1000 kPa ±34.5 kPa) and pressure tested at 350 psig (2413 kPa) at final unit assembly.

G.	Refrigeration Components:

Refrigerant circuit components shall include replaceable-core filter drier, moisture indicating sight glass, electronic expansion valve, discharge service valves and liquid line service valves, and complete operating charge of both refrigerant R-134a and compressor oil.

H.	Controls, Safeties, and Diagnostics:

1.	Unit controls shall include the following minimum components:

a.	Microprocessor with non-volatile memory. Battery backup system shall not be accepted.

b.	Separate terminal block for power and controls.

c.	Separate 115-v power supply to serve all controllers, relays, and control components.

d.	ON/OFF control switch.

e.	Replaceable solid-state controllers.

f.	Pressure sensors installed to measure suction, oil, economizer, discharge, and liquid pressure. Thermistors installed to measure cooler entering and leaving fluid temperatures and outside-air temperature.

2.	Unit controls shall include the following functions:

a.	Automatic circuit lead/lag.

b.	Capacity control based on leaving chilled fluid temperature and compensated by rate of change of return-fluid temperature with temperature set point accuracy to 0.1° F (0.05° C).

c.	Limiting the chilled fluid temperature pull-down rate at start-up to an adjustable range of 0.2° F to 2° F (0.1 to 1.1° C) per minute to prevent excessive demand spikes at start-up.

d.	Seven-day time schedule.

e.	Leaving chilled fluid temperature reset from return fluid and outside air temperature.

f.	Chilled water pump start/stop control.

g.	Chiller control for parallel chiller applications without addition of hardware modules and control panels (requires thermistors).

h.	Timed maintenance scheduling to signal maintenance activities for strainer maintenance and user-defined maintenance activities.

i.	Low ambient protection to energize cooler  heaters (if installed).

j.	Single step demand limit control activated by remote contact closure.

k.	Night time sound mode to reduce the sound of the machine by a user-defined schedule.

3.	Diagnostics:

a.	The control panel shall include, as standard, a display:

1)	Seven-inch color touch screen display with stylus.

2)	Display shall allow a user to navigate through menus, select desired options and modify data.

b.	Features of the display shall include:

1)	Multiple connection ports for USB, Ethernet, LEN (local equipment network), and Carrier Comfort Network® (CCN)  connections.

2)	Web connectivity for remote access to configuration, alarm, operation, and other menu functions.

3)	Automatic reporting of unit performance and operation available via internet.

4)	Ability to graphically plot trends of system performance and conditions over time.

5)	Graphical summary display of current chiller operation and water conditions.

6)	Display shall allow access to configuration, maintenance, service, set point, time schedules, alarm history, and status data.

7)	Three levels of password protection against unauthorized access to configuration and maintenance information, and display set up parameters.

8)	Full compatibility with the Carrier Comfort Network (CCN) system to provide email alarm notification and to provide network capability to fully monitor and control chiller.

9)	Display shall be capable of displaying the last 50 alarms with clear full text description and time and date stamp, and will store a snapshot of operating conditions before and after the 20 most recent alarms.

10)	Display run hours and number of starts for machine and individual compressors.

11)	Display current draw for each circuit compressor and fans.

12)	Capability of displaying the output (results) of a service test. Service test shall verify operation of each circuit fan and compressor, EXV (electronic expansion valve), switch, and sensors before chiller is started

13)	The control system shall allow software upgrade without the need for new hardware modules.

4.	Safeties:

a.	Unit shall be equipped with thermistors and all necessary components in conjunction with the control system to provide the unit with the following protections:

1)	Loss of refrigerant charge.

2)	Reverse rotation.

3)	Low chilled fluid temperature.

4)	Motor overtemperature.

5)	High pressure.

6)	Electrical overload.

7)	Loss of phase.

8)	Loss of chilled water flow.

b.	Condenser-fan motors shall have internal overcurrent protection.

I.	Operating Characteristics:

1.	Unit, without modification, shall be capable of starting and running at outdoor ambient temperatures from 32 F (0° C) to 125 F (52 C) for all sizes.

2.	Unit shall be capable of starting up with 95 F (35 C) entering fluid temperature to the cooler.

3.	After power restoration, and with the Capacity Recovery™ feature (a standard controls feature) enabled, unit shall be capable of full capacity recovery in less than 5 minutes.

J.	Motors:

Condenser-fan motors shall be totally enclosed, 6-pole, air over, variable speed, 3-phase type with permanently lubricated bearings and Class F insulation.

K.	Electrical Requirements:

1.	Unit primary electrical power supply shall enter the unit at a single location (all chiller voltage/size combinations shall have the ability to accommodate 2 power supplies to meet job-specific requirements).

2.	Primary electrical power supply shall be rated to operate up to 125 F (52 C) ambient           temperature for all models.

3.	Unit shall operate on 3-phase power at the voltage shown in the equipment schedule.

4.	Control points shall be accessed through terminal block.

5.	Unit shall be shipped with factory control and power wiring installed.

6.	Unit shall have a standard SCCR (short circuit current rating) value of 10 kA.

L.	Chilled Water Circuit:

1.	Chilled water circuit shall be rated for 300 psig (2068 kPa).

2.	Thermal dispersion proof of flow switch shall be factory installed and wired.

M.	Special Features:

Certain standard features are not applicable when the features designated by * are specified. For      assistance in amending the specifications, contact your Carrier representative.

1.	DX (Direct Expansion) Cooler Option:

a.	Shell-and-tube type, direct expansion.

b.	Tubes shall be internally enhanced seamless-copper type rolled into tube sheets.

c.	Shall be equipped with Victaulic-type water connections.

d.	Shell shall be insulated with 3/4-in. (19 mm) PVC foam (closed-cell) with a maximum K factor of 0.28.

e.	Design shall incorporate a minimum of 2 independent direct-expansion refrigerant circuits.

f.	Cooler shall be rested and stamped in accordance with ASME Code for a refrigerant working side pressure of 220 psig (1517 kPa). Cooler shall have a maximum water-side pressure of 300 psig (2068 kPa).

g.	Cooler shall be provided with a factory-installed flow switch.

2.	Unit-Mounted Non-Fused Disconnect:

Unit shall be supplied with factory-installed, lockable, non-fused electrical disconnect for main power supply.

3.	Optional Condenser Coil Materials:

a.	E-coated microchannel coils:

E-coated aluminum microchannel coil shall have a flexible epoxy polymer coating uniformly applied to all coil external surface areas without material bridging between fins or louvers. Coating process shall ensure complete coil encapsulation, including all exposed fin edges. E-coat shall have a thickness of 0.8 to 1.2 mil with top coat having a uniform dry film thickness from 1.0 to 2.0 mil on all external coil surface areas including fin edges. E-coated coils shall have superior hardness characteristics of 2H per ASTM D3363-00 and cross hatch adhesion of 4B-5B per ASTM D3359-02. Impact resistance shall be up to 160 in./lb (ASTM D2794-93). E-coated coil shall have superior impact resistance with no cracking, chipping, or peeling per NSF/ANSI 51-2002 Method 10.2. E-coated aluminum microchannel coils shall be capable of withstanding an 8,000-hour salt spray test in accordance with the ASTM (American Society for Testing and Materials) (U.S.A.) B-117 Standard.

b.	Aluminum fin/copper-tube coils:

Coil shall be constructed of seamless copper tubes mechanically bonded to aluminum fins. Fins shall have wavy enhancements. These condenser coils are recommended with remote cooler applications. These coils are not recommended for corrosive environments.

c.	Pre-coated aluminum-fin coils:

Shall have a durable epoxy-phenolic coating to provide protection in mildly corrosive coastal environments. Coating shall be applied to the aluminum fin stock prior to the fin stamping process to create an inert barrier between the aluminum fin and copper tube. Epoxy-phenolic barrier shall minimize galvanic action between dissimilar metals.

d.	Copper-fin coils:

Shall be constructed of copper fins mechanically bonded to copper tubes and copper tube sheets. Galvanized steel tube sheets shall not be acceptable. A polymer strip shall prevent coil assembly from contacting sheet metal coil pan to minimize potential for galvanic corrosion between the coil and pan. All copper construction shall provide protection in moderate coastal applications.

e.	E-coated aluminum-fin coils:

Shall have a flexible epoxy polymer coating uniformly applied to all coil surface areas without material bridging between fins. Coating process shall ensure complete coil encapsulation. Color shall be high gloss black with gloss — 60° of 65-90% per ASTM D523-89. Uniform dry film thickness from 0.8 to 1.2 mil on all surface areas including fin edges. Superior hardness characteristics of 2H per ASTM D3363-92A and cross hatch adhesion of 4B-5B per ASTM D3359-93. Impact resistance shall be up to 160 in./lb (ASTM D2794-93). Humidity and water immersion resistance shall be up to minimum 1000 and 250 hours respectively (ASTM D2247-92 and ASTM D870-92). Corrosion durability shall be confirmed through testing to no less than 3000 hours salt spray per ASTM B117-90. Coil construction shall be aluminum fins mechanically bonded to copper tubes.

f.	E-coated copper-fin coils:

Shall have a flexible epoxy polymer coating uniformly applied to all coil surface areas without material bridging between fins. Coating process shall ensure complete coil encapsulation. Color shall be high gloss black with gloss — 60° of 65-90% per ASTM D523-89. Uniform dry film thickness from 0.8 to 1.2 mil on all surface areas including fin edges. Superior hardness characteristics of 2H per ASTM D3363-92A and cross hatch adhesion of 4B-5B per ASTM D3359-93. Impact resistance shall be up to 160 in./lb (ASTM D2794-93). Humidity and water immersion resistance shall be up to minimum 1000 and 250 hours respectively (ASTM D2247-92 and ASTM D870-92). Corrosion durability shall be confirmed through testing to no less than 3000 hours salt spray per ASTM B117-90. Coil construction shall be copper fins mechanically bonded to copper tube sheets. Galvanized steel tube sheets shall not be acceptable. A polymer strip shall prevent coil assembly from contacting sheet metal coil pan to maintain coating integrity and minimize corrosion potential between the coil and pan.

4.	Energy Management Module:

A factory or field-installed module shall provide the following energy management capabilities: 4 to 20 mA signals for leaving fluid temperature reset, cooling set point reset or demand limit control; 2-step demand limit control (from 0% to 100%) activated by a remote contact closure; and discrete input for “Ice Done” indication for ice storage system interface.

5.	Condenser Coil Trim Panels:

Unit shall be supplied with factory-installed or field-installed coil covers.

6.	BACnet/Modbus Translator Control:

Unit shall be supplied with factory or field-installed interface between the chiller and a BACnet Local Area Network (LAN, i.e., MS/TP EIA-485). Field programming shall be required.

7.	LON Translator Control:

Unit shall be supplied with factory or field-installed interface between the chiller and a Local Operating Network (LON, i.e., LonWorks FT-10A ANSI/EIA-709.1). Field programming shall be required.

8.	Isolation Valve Option:

Unit shall be supplied with factory-installed isolation valve which provides a means of isolating the compressors from the cooler vessel, which is beneficial in servicing the chiller. The isolation option comes in various configurations depending on the cooler type (flooded or DX) and the installation region (Middle Eastern or elsewhere). On all units equipped with the flooded cooler which are not installed in the Middle East region, a liquid line service valve and a motorized discharge isolation valve are always provided per refrigerant circuit. For Middle Eastern regions only, a manual discharge valve is standard and a motorized discharge ball valve is optional. On units equipped with the optional DX cooler, the liquid line service valve and a manual discharge service valve is included in the isolation valve option, regardless of the region of installation. Regardless of which cooler option is employed, the selection of the isolation valve option results in chillers which are equipped with a liquid line service valve, a discharge service valve (motorized or manual type), and a series of valves on or near the cooler. The net effect is to provide isolation capability in the condenser area, the cooler area and the compressor area.

NOTE: The only situation in which the isolation of the condenser area allows the full charge to be stored in the condenser is when round tube, plate fin (RTPF) coils are employed.

9.	Suction Line Insulation:

Unit shall be supplied with suction line insulation. Insulation shall be tubular closed-cell insulation. This option shall be required with applications with leaving fluid temperatures below 30 F (–1.1 C) and recommended for areas of high dewpoints where condensation may be a concern.

10.	Control Transformer:

Unit shall be supplied with a factory-installed transformer that will allow supply control circuit power from the main unit power supply.

11.	GFI Convenience Outlet:

Shall be field-installed and mounted with easily accessible 115-v female receptacle. Shall include 4-amp GFI receptacle. Not available with 380-v units.

12.	Plus-One-Pass Cooler:

Unit shall be equipped with plus-one-pass cooler heads to be used with high delta T application. Applies to flooded coolers only.

13.	Minus-One-Pass Cooler:

Unit shall be equipped with minus-one-pass cooler heads with reduced water-side pressure drop for series flow dual chiller control or high chilled water flow applications. Applies to flooded coolers only.

14.	Security Grilles:

Unit shall be provided with factory (or field) installed painted grilles to protect the condenser, cooler and compressor.

15.	Upper Hail Guard:

Unit shall be equipped with a factory-installed option consisting of louvered panels on the ends of the machine which firmly fasten to the machine frame. These panels shall cover the unit from the top to the bottom of the coils, thus providing protection of the coils from hail damage.

16.	Full Hail Guard:

Unit shall be equipped with field-installed accessory consisting of hinged, louvered panels, which cover both ends of the unit. This accessory provides complete protection from hail.

17.	Full End Screen:

Unit shall be equipped with a factory-installed option consisting of louvered panels that cover the machine ends from top to bottom and firmly fasten to the machine frame. These end screens function as a privacy screen and also provide hail protection.

18.	Low Sound Package:

Unit shall be provided with sound attenuation package to include sheet metal enclosures with sound absorbing panels for each compressor.

19.	Remote Cooler Kit:

Allows remote installation of the cooler.

20.	Dual Chiller Accessory Kit:

For dual chiller applications (with units piped in parallel), unit shall be provided with the additional hardware (thermistors, wells, connectors) required for proper system operation.

21.	Seismic Certification:

A seismic kit is available which will result in a unit SDS (seismic design acceleration parameter) level of 2.4.