Product Name: Adjustable Frequency AC Drive for Variable Torque HVAC and Pumping Applications (1-50 hp at 208/230 V and 1-100 hp at 460 V)

### SECTION 26 29 23.11

### Adjustable Frequency Drives for HVAC and Pumping Applications

PART 1: GENERAL

1.01 SUMMARY

A.	This section provides specification requirements for solid-state, pulse-width modulated (PWM) Adjustable Frequency Drives, herein referred to as AC Drives, for use with NEMA® design AC motors.

B.	The AC Drive supplier shall furnish, field test, adjust and certify all installed AC Drives for satisfactory operation.

C.	Any exceptions/deviations to this specification shall be indicated in writing and submitted no less than one week prior to bid date.

1.02 REFERENCES

- ANSI®/NFPA® 70 - National Electrical Code® (NEC®).

- UL 508 - UL Standard for Safety Industrial Control Equipment.

- UL 508C - UL Standard for Safety Power Conversion Equipment.

- NEMA ICS 7.1

1.03 SUBMITTALS

A.	A submittal package, including drawings shall be furnished for the Engineers’ approval prior to factory assembly of the AC Drives. These packages shall consist of elementary power and control wiring diagrams on one drawing and enclosure outline drawings. The enclosure drawings shall include front and side views of the enclosures with overall dimensions and weights shown, and conduit entrance locations. Standard catalog specification sheets showing voltage, horsepower and maximum current ratings shall be furnished as part of the submittal package.

1.04 WARRANTY

A.	An 18-month warranty shall be provided on materials and workmanship from the date of shipment.

1.05 QUALITY ASSURANCE

A.	The manufacturer of the AC Drive shall be a certified ISO 9001 facility.

B.	The AC Drive and all associated optional equipment shall be UL Listed according to UL 508 C - Power Conversion Equipment. As verification, a UL label shall be attached on the inside of the combination enclosure.   A UL508A panel builders label does not meet specification.

C.	The AC Drive shall be designed, constructed and tested in accordance with UL, CSA, NEMA, and NEC standards.

D.	Every power converter shall be tested with an AC induction motor while loaded and temperature cycled within an environment chamber at 40 ˚C (104 ˚F).

## PART 2: PRODUCT

2.01 MANUFACTURERS

A.	The AC Drive shall be manufactured by Square D Schneider Electric or prior approved equal. Substitutions must be submitted in writing three weeks prior to original bid date with supporting documentation demonstrating that the alternative manufacturer meets all aspects of the specifications herein.   Supporting documentation should include a line by line review of this specification indicating if the substitution meets or does not meet each item in this specification.

2.02 GENERAL DESCRIPTION

A.	The AC Drive shall convert the input AC mains power to an adjustable frequency and voltage.

B.	The input power section shall utilize a full wave bridge design incorporating diode rectifiers. The diode rectifiers shall convert fixed voltage and frequency, AC line power to fixed DC voltage.

C.	The output power section shall change fixed DC voltage to adjustable frequency AC voltage.

D. 	The adjustable frequency NEMA 1 drive package shall consist of a circuit breaker disconnect, line reactor, EMI/RFI filter (if drive design requires RFI interference protection), 2 contactor bypass, 120V control transformer, control circuit terminal board for digital and analog field wiring.  AC line fuses do not meet specification.

- The drive door shall have mounted and wired, Hand-Off-Auto switch, Manual Speed Potentiometer and AFC-Off-Bypass switch.

- The entire drive package, including the bypass starter circuit shall be UL508C listed and coordinated with NEMA ICS 7.1.  A UL508A panel builders label does not meet specification.

2.03 CONSTRUCTION

A.	The AC Drive power converter shall be enclosed in a NEMA Type 1 enclosure with a circuit breaker disconnect, user terminal strip connections and bypass controls. The enclosure shall provide dedicated user terminals for power and control device connection.

- Provisions shall be included for locking the disconnect in the OFF position with a padlock.

- All enclosure and heat sink fans shall be accessible from the front and shall not require the removal of the AC drive power converter for fan replacement.

2.04 APPLICATION DATA

A.	The AC Drive shall be sized to operate a variable torque load.

B.	The speed range shall be from a minimum speed of 1.0 Hz to a maximum speed of 72 Hz.

2.05 ENVIRONMENTAL RATINGS

- The AC Drive shall meet IEC 60664-1 Annex A and NEMA ICS 1, UL, and CSA standards.

- The AC Drive shall be designed to operate in an ambient temperature from -10 to 40 ˚C (14 to 104 ˚F).

- AC Drives in Type 3R enclosures shall be designed to operate in an ambient temperature from -10 to 50 ˚C (14 to 122 ˚F) and in full sunlight.

C.	The storage temperature range shall be -25 to 65 ˚C (-13 to 149 ˚F).

D.	The maximum relative humidity shall be 95%, non-condensing.

E.	The AC Drive shall be rated to operate at altitudes less than or equal to 3300 ft (1000 m). For altitudes above 3300 ft (1000 m), the AC Drive should be de-rated per drive specifications.

F.	The AC Drive shall meet the IEC 60721-3-3-3M3 operational vibration specification.

G. 	The AC Drive shall be Seismic Qualified to 2000 IBC Level 3 “Extreme” rating with an  Importance Factor 1p=1.5

2.06 RATINGS

A.	The AC Drive shall be designed to operate at the input line voltage indicated on the equipment schedule.

B.	The AC Drive shall operate from an input frequency range of 60 Hz (±) 5%.

C.	The displacement power factor shall not be less than .98 lagging under any speed or load condition.

D.	The efficiency of the AC Drive at 100% speed and load shall not be less than 97%.

E.	The variable torque rated AC Drive over current capacity shall be not less than 110% for 1 minute.

F.	The output carrier frequency of the AC Drive shall be programmable at 0.5, 1, 2, 4 or 8 kHz. In addition, the output carrier frequency shall be randomly modulated about the selected frequency.

2.07 PROTECTION

A.	Upon power-up, the AC Drive shall automatically test for valid operation of memory, loss of analog reference input, loss of communication, DC-to-DC power supply, control power and pre-charge circuit.

B.	The enclosure shall provide a fully coordinated 100,000 AIC current rating marked on the enclosure nameplate. Short circuit coordination to UL 508C Power Conversion Equipment and NEMA ICS 7.1.

C.	The AC Drive shall be protected against short circuits, between output phases and to ground.

D.	The AC Drive shall have a minimum AC undervoltage power loss ride-through of 200 milliseconds (12 cycles).

E.	The AC drive shall have a programmable ride-through function, which will allow the logic to maintain control for a minimum of one-second (60 cycles) without faulting.

F.	For a fault condition other than a ground fault, short circuit or internal fault, an auto restart function will provide up to 6 programmable restart attempts. The time delay before restart attempts will be 30 seconds.

G.	Upon loss of the analog process follower reference signal, the AC Drive shall be programmable to display a fault.

H.	The AC Drive shall have a solid-state UL 508C listed overload protective device and meet IEC 60947.

I.	The output frequency shall be software enabled to fold back when the motor is overloaded.

J.	There shall be three skip frequency ranges that can be programmed to a bandwidth of  2.5 Hz.

2.08 ADJUSTMENTS & CONFIGURATIONS

A.	The AC Drive will be factory programmed to operate all specified optional devices.

B.	The acceleration and deceleration ramp times shall be adjustable from 0.05 to 999.9 seconds.

C.	The memory shall retain and record run status and fault type of the past eight faults.

D.	The software shall have an energy economy function that, when selected, will reduce the voltage to the motor when selected for variable torque loads. A constant volts/Hz ratio will be maintained during acceleration. The output voltage will then automatically adjust to meet the torque requirement of the load.  Selectable volts/Hz ratio patterns does not meet specification, the function must be automatically optimized.

2.09 KEYPAD DISPLAY INTERFACE

A.	A keypad display interface shall offer the modification of AC Drive adjustments through a touch keypad. All electrical values, configuration parameters, I/O assignments, application and activity function access, faults, local control, and adjustment storage, and diagnostics shall be accessible.

B.	The AC Drive model number, torque type, software revision number, horsepower, output current, motor frequency and motor voltage shall be listed on the drive identification portion of the LCD display.

- The keypad display shall have a hardware selector switch that allows the keypad to be locked out from unauthorized personnel.

2.10 OPERATOR CONTROLS

A.	The control power for the digital inputs and outputs shall be 24 Vdc.

B.	The internal power supply shall incorporate automatic current fold-back that protects the internal power supply if incorrectly connected or shorted. The transistor logic outputs will be current limited and will not be damaged if shorted.

C.	Pull-apart terminal strips shall be used on all logic and analog signal connections in the power converter

- Two voltage-free relay output contacts will be provided. One of the contacts will indicate AC Drive fault status. The other contact shall indicate a drive run status.

- The combination enclosure shall have the following dedicated operator controls:

1.	Hand-Off-Auto switch

2.	Manual Speed Potentiometer

3.	AFC-Off-Bypass switch

- The combination enclosure shall include terminal point connection for fire /freeze state interlock, to prevent drive [or bypass] operation. The interlock must shut down the motor in the drive and bypass modes.

2.11 SERIAL COMMUNICATION

- The AC Drive shall have serial communications capability.

2.12 DRIVE ISOLATION AND BYPASS CONTACTORS

- The AC Drive shall include mechanically and electrically interlocked isolation and bypass contactors complete with a Class 20 thermal overload relay, circuit breaker disconnect, control circuit transformer and AFC/OFF/BYPASS switch.

- The operator shall have full control of the bypass starter by operation of the AFC/OFF/BYPASS selector switch.

- In the AUTOMATIC mode of operation the bypass contactors shall be sequenced by the 120-volt rated auto start contact provided by the user.

- The isolation contactor for the bypass shall be sequenced to provide motor isolation during a drive ready state of operation.

2.13 HARMONIC MITIGATION

A.	Each drive shall include a line reactor mounted inside the drive enclosure to reduce power system harmonics and provide power quality protection for the drive.  DC bus chokes do not meet specification and shall not be substituted.

# PART 3: INSTALLATION

3.01	INSPECTION

A.	Verify that the location is ready to receive work and the dimensions are as indicated.

3.02	PROTECTION

A.	Before and during the installation, the AC Drive equipment shall be protected from water and site contaminants.

3.03	INSTALLATION

A.	Installation shall be in compliance with manufacturer's instructions, drawings and recommendations.

B.	The AC Drive supplier shall provide a representative to inspect the contractor's installation, test and start-up the AC Drive(s) furnished under this specification.

3.04	TRAINING

A.	On-site training shall be provided as part of the start-up service.

3.05	DOCUMENTATION

A.	The AC Drive supplier shall supply a comprehensive 8-1/2 x 11-inch bound instruction and installation manual that includes wiring diagrams, layout diagrams, and outline dimensions. This manual must be 3-hole punched for insertion in a shop manual supplied by the installing contractor.

Copies of this specification are available from the Square D/Schneider Electric website: www.us.SquareD.com.